METRO DETROIT AIRPORT — IT CENTER

IT Center Data Center & NOC Build-Out

Project Charter · Communication Plan · Commissioning & Handover Plan

| Project Type | Construction / Infrastructure |
| --- | --- |
| Prepared By | Lisa Lewandowski, Project Manager |
| Date | Illustrative portfolio project — dated for a 14-month build cycle |
| Document Status | Baselined — Illustrative / Self-Directed Practice Project |

PORTFOLIO SCENARIO — This is an illustrative, self-directed practice project prepared as candidate work for an infrastructure/IT Project Manager role. It is not a record of an actual Metro Detroit Airport engagement; it demonstrates the PM documentation standard the author would run on a comparable data-center construction project. Companion project: “02 — Network & Systems Modernization” (Technology), which fits out this facility once construction is complete.

# 1. Project Charter

## 1.1  Purpose / Business Case

The IT Center's existing server room is converted office space with no redundant power or cooling path, creating a single point of failure for systems that support baggage handling, passenger processing, and security operations. This project constructs a dedicated ~9,000 sq. ft. data center / network operations center (NOC) addition adjacent to the existing IT Center building, with N+1 power and cooling, to consolidate and protect airport operations technology infrastructure and to provide the physical space the companion Network & Systems Modernization project will fit out and cut over into.

## 1.2  Objectives

- Deliver a code-compliant, Tier III-aligned data center/NOC addition (~9,000 sq. ft.) within the approved GMP budget and schedule.

- Provide N+1 redundant power (dual utility feed, UPS, standby generator) and precision cooling to remove existing single points of failure.

- Reach Substantial Completion in time to support the Network & Systems Modernization project's fit-out and cutover window.

- Complete construction with zero lost-time safety incidents and pass all Authority Having Jurisdiction (AHJ) inspections on first submission.

## 1.3  Success Criteria / KPIs

- Substantial Completion within 10 business days of the baselined target date.

- Final construction cost within 5% of the approved Guaranteed Maximum Price (GMP).

- Zero OSHA-recordable incidents across the construction duration.

- 100% of Level 1–4 commissioning checklist items signed off before handover.

- Power and cooling capacity validated against design load (kW/rack) prior to handover to IT Operations.

## 1.4  Sponsor & Project Team

Executive Sponsor:  Director of Facilities & Infrastructure, Metro Detroit Airport IT Center

Project Manager:  Lisa Lewandowski

Core team: General Contractor (GC) and site superintendent, MEP Engineer of Record, Commissioning Agent, Electrical and Mechanical subcontractors, Low-Voltage/Security Systems Integrator. Cross-functional stakeholders: Airport Facilities, IT Center Operations (receiving owner), Airport Security/Badging Office, local Building Department/AHJ, and the Airport Authority Capital Improvement Program (CIP) office.

## 1.5  Scope

In Scope

- Site work, foundation, and structural shell for the ~9,000 sq. ft. addition adjacent to the existing IT Center building.

- Electrical: dual utility feeds, N+1 UPS, standby generator, PDUs, and distribution to server rack locations.

- Mechanical: precision CRAC/CRAH cooling, hot/cold aisle containment, redundant chiller capacity.

- Clean-agent fire suppression and pre-action sprinkler system per code.

- Raised access flooring, cable tray, and structured-cabling pathways (rough-in only).

- Physical security: badge access control, mantrap vestibule, CCTV, and environmental monitoring (temperature/humidity/water leak detection).

- Permitting, AHJ inspections, and full commissioning (Cx) aligned to Uptime Institute / ASHRAE TC 9.9 practice.

Out of Scope

- Server, network, and systems hardware installation and cutover (covered under the companion Network & Systems Modernization project).

- Structured cabling termination and testing beyond pathway rough-in.

- Airside/airfield construction and passenger-facing terminal work.

## 1.6  High-Level Milestones

| Milestone | Target Date | Key Deliverable |
| --- | --- | --- |
| Design Development & Permitting Complete | Month 3 | Stamped construction drawings; permits issued |
| Sitework & Foundation Complete | Month 5 | Foundation inspection passed |
| Structural Shell & Building Dry-In | Month 7 | Roof/envelope watertight |
| MEP Rough-In Complete | Month 9 | Power, cooling, fire-suppression rough-in inspections passed |
| Raised Floor, Security & Finishes Complete | Month 11 | Punch list issued |
| Commissioning (Cx) Complete | Month 13 | Level 1–4 Cx checklist signed off |
| Substantial Completion & Handover to Operations | Month 14 | Certificate of Occupancy; O&M turnover to IT Ops |

## 1.7  Assumptions

- The adjacent, existing IT Center building remains fully operational throughout construction with no planned outages.

- The utility company confirms adequate feeder capacity for the dual-feed design during Design Development.

- Long-lead equipment (generator, UPS, chillers) is ordered at Notice to Proceed to protect the schedule.

- Local AHJ permitting timelines track historical averages for comparable Authority capital projects.

## 1.8  Constraints

- Construction must not disrupt live airport operations systems currently housed in the adjacent legacy server room.

- The site is bounded by existing airport perimeter security and badge-access zones, limiting contractor laydown area.

- Budget is fixed at GMP; any scope change requires an approved Change Order before work proceeds.

- All site personnel require TSA/airport security badging; work windows may be restricted near active ramp areas.

## 1.9  Budget Summary

| Category | Amount |
| --- | --- |
| Total Approved GMP Budget | $4,250,000 |
| Contingency Reserve | $340,000 (8%) |
| Funding Source | Airport Authority Capital Improvement Program (CIP) — IT Infrastructure line item |

## 1.10  Approval

| Role | Name | Signature / Date |
| --- | --- | --- |
| Executive Sponsor — Director, Facilities & Infrastructure | [Name] | [Signature / Date] |
| Project Manager | Lisa Lewandowski | [Signature / Date] |
| IT Center Operations Manager (Receiving Owner) | [Name] | [Signature / Date] |

# 2. Stakeholder Communication Management Plan

Communication is structured around the GC's weekly site rhythm and the Authority's monthly capital-program governance. All schedule, budget, RFI, and submittal status lives in the PM Tracking Workbook; the PM is the single point of contact between the project team, subcontractors/vendors, and Authority stakeholders.

| Audience | Information Needs | Method | Frequency | Owner |
| --- | --- | --- | --- | --- |
| Airport Authority Capital Committee | Budget vs. GMP, schedule health, major risks | Monthly capital program review | Monthly | PM |
| Facilities & Security Leadership | Site access, badging, safety incidents | Steering meeting | Monthly | PM |
| GC / Subcontractors | Schedule, RFIs, submittals, inspections | Site progress meeting | Weekly | PM |
| IT Center Operations (receiving owner) | Handover readiness, Cx results, O&M turnover | Coordination meeting | Bi-weekly (ramps up pre-handover) | PM |
| AHJ / Building Department | Inspection scheduling and results | Formal inspection requests | Per milestone | GC / PM |

# 3. Commissioning & Facility Handover Plan

Commissioning follows a four-level model before the facility is handed to IT Operations and cleared for the companion technology fit-out project to begin.

| Activity | Audience | Method | Timing | Owner |
| --- | --- | --- | --- | --- |
| Level 1 — Equipment startup & static checks | Cx Agent, subcontractors | Vendor startup + Cx witness | Month 12 | Commissioning Agent |
| Level 2 — Functional performance testing (load bank) | MEP Engineer, Cx Agent | Load-bank test of UPS/generator/cooling | Month 12–13 | Commissioning Agent |
| Level 3 — Integrated systems test (utility failure/generator transfer) | Facilities, IT Ops observers | Simulated outage test | Month 13 | Commissioning Agent |
| Level 4 — Integrated test under simulated IT load | IT Ops, Facilities | Full-load simulation | Month 13 | Commissioning Agent |
| Facilities O&M training walkthrough | IT Center Operations, Facilities staff | Guided walkthrough + O&M manuals | Month 14 | GC / PM |
| As-built documentation & warranty turnover | IT Center Operations | Document package handover | Month 14 | PM |